Product program / Loudspeaker / Wall

BS-1034EN

The speaker shall be a wall-mount speaker design that harmonizes with the venue's architecture and interior decor. The proportion shall be based on the Golden Ratio. The speaker shall be ideal for BGM, announcement and voice evacuation applications due to wide frequency range.
The speaker unit shall combine a 12 cm (5") cone type low frequency speaker with a balanced dome-type tweeter. The unit shall be wall mountable with a supplied plug-in speaker receptacle accessory. The input connector shall be a M4 screw terminal, with an 11 mm distance between barriers. A fire-resistant screw terminal block with thermal fuse should be supplied. Input impedance shall be easily adjustable with rotary switch on the rear side of the speaker.
The speaker shall include a transformer having multiple taps (10 W, 5 W, 3 W, 1 W at 100 V line and 10 W, 5 W, 2.5 W, 1.5 W, 0.5 W at 70 V line) adjustable. The output sound pressure level at a distance of 1 m with a 1 W input level applied shall be 89 dB SPL. The speaker shall have a frequency response of 120 – 20 kHz (-20 dB). The speaker shall have an ingress protection for indoor applications: IEC 60529 / EN 60529 drip-proof rating of IP21C. The speaker enclosure shall be constructed of fire resistant HIPS resin that has fire resistant grade UL94V-0. The grille shall be constructed of surface-treated steel plate net. The speaker shall be available in off-white colour (RAL 9010 or equivalent). The unit shall have dimensions of 210 (W) × 330 (H) × 80 (D) mm (8.27" × 12.99" × 3.15"), and a weight of 1.4 kg (3.09 lb). The speaker shall be certified according to EN 54-24 with CPD Number 0359-CPD-0102, certified according to ISO 7240-24.
The speaker shall be a TOA model BS-1034EN.