Product program / Loudspeaker / Projector

CS-304    EU

<div>The speaker shall be a wide-range weatherproof horn speaker suitable for paging, background music and tone signaling distribution. The speaker component shall be a 12 cm (4.72")&nbsp; cone-type speaker, treated for weather-resistance. Rated input shall be 30 W. The speaker shall include a transformer having multiple taps (10W, 20W, 30W at 100 V and 5W, 10W, 15W, 30W at 70V). The sensitivity at a distance of 1m with a 1W input level applied shall be 98 dB. The speaker shall have a frequency response of 120 - 15 kHz. Horizontal and vertical dispersion at –6 dB below the on-axis reference at 2 kHz shall be 100° (H) x 85° (V).</div><div>The speaker shall have a IEC 529 splash-proof rating of IP65. The speaker shall have an operating temperature of -20° C to +55° C (-4° F to 131° F). The speaker enclosure shall be constructed of ABS resin and coated with polyurethane resin paint to resist long-term exposure to ultraviolet light. The grille shall be constructed of a protective aluminum net to prevent damage, gray paint. All mounting hardware, including screws and bolts, shall be stainless steel, which protects the speaker from corrosion. The wide-range weatherproof paging horn shall include an integral speaker cable, 2-core cabtyre cord with diameter of 6 mm (0.24") diameter.</div><div>Dimensions shall be 366(W) x 230(H) x 272(D) mm (14.40” x 9.06” x 10.71”). Weight shall be 3.1 kg (6.83 lb.).</div><div>The wide-range weatherproof horn speaker shall be TOA model CS-304.</div>