Product program / Loudspeaker / Ceiling

PC-1860BS

The loudspeaker shall be of in-ceiling type design and shall consist of two parts, comprising of an inner mesh grille and chassis with an integral loudspeaker with no visible fixings and a discreet outer bezel of only 5 mm. The second part shall be a steel constructed fire dome for the prevention of smoke or fire spreading through ceiling voids in an emergency situation.
Installation shall be via a separate spring catch latching mechanism allowing it to be mounted in a ceiling with a thickness of between 5 – 25 mm (0.2" – 0.98").
A template shall be provided to assist in cutting mounting holes.
The loudspeaker shall incorporate a single 12 cm (5”) full range cone-type transducer with a smooth frequency response of 170 Hz to 20 kHz with a wide-angle dispersion.
The loudspeaker shall produce a Sound Pressure Level (SPL) of 95 dB (measured between 500 Hz – 5 kHz of pink noise) on axis at 1 meter with a power input of 1 watt and 81dB (measured between 100Hz – 10kHz of pink noise) on axis at 4 meters with
a power input of 1 watt. The loudspeaker shall be capable of producing 6 watts (for 100 V Line) and 3 watts (for 70 V Line) of power.
The loudspeaker shall be fitted with a factory mounted transformer with easy selectable power tappings of 6 W, 3 W, 1.5 W and 0.8 W when using 100 V Line and 3 W, 1.5 W, 0.8 W and 0.4 W when using 70 V Line. Push-in-type connectors shall make cable connection quick and easy and shall allow bridge connection when necessary.
The ceiling mount loudspeaker shall incorporate suitable anchoring points, as an additional precautionary measure, allowing an attachment of a safety wire to avoid displacement.
The dimensions shall be φ180 × 100 mm (d) (7.09" x 3.94") weighing 1.1 kg (2.43 lb.)
The finish of the loudspeaker shall be: Baffle: steel plate, white (RAL 9016 equivalent). Grille: Steel net, white (RAL 9016 equivalent). Mounting bracket: steel plate.
The ceiling mount loudspeaker shall be certified according to the following standards: European Standard EN 54-24: 2008, International Standard ISO 7240-24: 2010 and shall comply with British Standard BS-5839-8: 2013.