Product program / Loudspeaker / Ceiling

PC-1860EN

The loudspeaker shall be of in-ceiling type design, with a full lightweight metal construction with no visible fixings and a discreet outer bezel of only 5 mm.
Installation shall be via pre-mounted springs allowing it to be mounted in a ceiling with a thickness of between 5 – 25 mm (0.2" – 0.98").
A template shall be provided to assist in cutting mounting holes.
The loudspeaker shall incorporate a single 12 cm (5”) full range cone-type transducer with a smooth frequency response of 80 Hz to 20 kHz measured on axis.
The loudspeaker shall produce a Sound Pressure Level (SPL) of 94 dB on axis at 1 meter with a power input of 1 watt and 80dB (measured between 100Hz – 10kHz of pink noise) on axis at 4 meters with a power input of 1 watt. The loudspeaker shall be
capable of producing 6 watts (for 100 V Line) and 3 watts (for 70 V Line) of power.
The loudspeaker shall be fitted with a factory mounted transformer with easy selectable power tappings of 6 W, 3 W, 1.5 W and 0.8 W when using 100 V Line and 3 W, 1.5 W, 0.8 W and 0.4 W when using 70 V Line. Push-in-type connectors capable of handling solid cable: 0.5 – 3 mm² (AWG 20 – 12) shall be employed and shall allow bridge connection when necessary.
The dimensions shall be φ180 × 70 mm (d) (7.09" x 2.76") weighing 560 g (1.23 lb.)
The finish of the loudspeaker shall be: Baffle: steel plate, white (RAL 9016 equivalent). Grille: Steel net, white (RAL 9016 equivalent). Mounting bracket: steel plate.
The ceiling mount loudspeaker shall be certified according to the following standards: European Standard EN 54-24: 2008, International Standard ISO 7240-24: 2010 and shall comply with British Standard BS-5839-8: 2008.