Product program / Loudspeaker / Ceiling

PC-1867F  EU

The ceiling mount loudspeaker shall consist of two parts, comprising of an inner mesh grille and chassis with an integral loudspeaker with no visible fixings. Installation shall be via pre-mounted springs. The second part shall be a steel constructed fire dome for the prevention of smoke or fire spreading through ceiling voids in an emergency situation.
The loudspeaker shall incorporate a single 12cm (5”) full range transducer.
The unit shall have a smooth frequency response between 100 Hz to 16 kHz (without fire dome) measured on axis. The loudspeaker shall produce a Sound Pressure Level (SPL) of 90 dB on axis at 1 meter with a power input of 1 watt and shall be capable of producing 6 watts (for 100 V Line) and 3 watts (for 70 V Line) of power. The unit shall be fitted with a factory mounted transformer with power tapping’s of 6 W, 3 W, 1.5 W and 0.8 W when using 100 V Line and 3 W, 1.5 W, 0.8 W and 0.4 W when using 70 V Line. Push-in connectors shall make cable connection easy and quick.
The dimensions shall be φ180 × 11 mm (exposed section) x 110 (D) mm (φ7.09" × 0.43" x 4.33") weighing 1.4 kg (3.09 lb.) (Bracket and fire dome included). The finish of the loudspeaker shall be: Baffle: Aluminium, white (RAL 9016 equivalent). Grille: Aluminium mesh, white (RAL 9016 equivalent). Dome mounting bracket: Steel plate, trivalent chromate treatment plating. Fire dome: Steel plate, black.