Product program / Loudspeaker / Projector

PJ-154BS

<div>The speaker shall combine a bass-reflex 12 cm (5") cone type, with a balanced-dome tweeter, suitable for ceiling and wall mounting. It is also designed for use in voice evacuation systems. Input impedance shall be easily adjustable with rotary switch on the upper side of the speaker. The speaker shall include a transformer having multiple taps (5 W, 10 W, 15 W at 100 V and 2.5 W, 5 W, 7.5 W at 70 V) adjustable.&nbsp;</div><div>The output sound pressure level at a distance of 1m with a 1W input level applied shall be 91 dB SPL. The speaker shall have a frequency response of 70 – 20 kHz (-20 dB). The speaker shall have an ingress protection for indoor applications: IEC 60529 / EN 60529 drip-proof rating of IP21C. Fire Rated Cable can be connected to the speaker terminal box via 20 mm cable gland. 2 × fire-resistant steatite screw terminal blocks with thermal fuse in the speaker terminal box allows secure cable connections and bridge wiring, a shielded 4 core fire-resistant suspension cable avoid risk of failure of speaker line and provide secure mounting feature with internal flame-resistant insulated cables.</div><div>The speaker enclosure shall be constructed of HIPS resin. The grille shall be constructed of surface-treated steel plate net. The speaker shall be available in off-white colour. The speaker unit shall have dimensions of ø186 × 251 (H) mm (ø7.32” × 9.88”), and a weight of 2.1 kg (4.63 lb).</div><div>The speaker shall be certified according to EN 54-24 with CPD Number 0359-CPD-0106, certified according to ISO 7240-24 and in compliance with the British Standard BS 5839-8.</div><div>The speaker shall be a TOA model PJ-154BS.</div>