Product program / Loudspeaker / Column

TZ-200BS-EB

Column speaker, 20 W, EN54

The speaker shall be a wall-mount column speaker designed for indoor and outdoor installation. The speakers shall come with a screw type loop through steatite terminal block and thermal fuse. It shall be certified according to the European Standard EN 54-24:2008 and compliant with the British Standard BS 5839-8:2008.

Rated Input: Min. 20 W

Rated Impedance: 100 V line: Min. 500 Ω (20 W), 1 kΩ (10 W), 2 kΩ (5 W)
&nbsp; &nbsp; &nbsp; &nbsp; &nbsp; &nbsp; &nbsp; &nbsp; &nbsp; &nbsp; &nbsp; &nbsp; &nbsp; &nbsp; &nbsp; &nbsp; &nbsp; &nbsp; &nbsp;70 V line: Min. 500 Ω (10 W), 1 kΩ (5 W), 2 kΩ (2.5 W)

Frequency Response: Max. 130 Hz – min. 20 kHz (peak -20 dB)

Sensitivity: Min. 92 dB (1 W, 1 m, 100 – 10 kHz, pink noise)

Max. SPL: Min. 105 dB (20 W, 1 m, 100 – 10 kHz, pink noise)

Coverage Angle (-6 dB): 
&nbsp; &nbsp; &nbsp; &nbsp; &nbsp; &nbsp; &nbsp; &nbsp; &nbsp; &nbsp; &nbsp; &nbsp; &nbsp; &nbsp; &nbsp; &nbsp; &nbsp; &nbsp; &nbsp; &nbsp; &nbsp; &nbsp; &nbsp; 500 Hz: Min. 360&deg; horizontal, min. 100&deg;  vertical
&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp; 1 kHz: Min. 185&deg; horizontal, min. 45&deg; vertical
&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp; 2 kHz: Min. 130&deg; horizontal, min. 25&deg; vertical
&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp; 4 kHz: Min. 100&deg; horizontal, min. 20&deg; vertical

Operating Temperature: Max. -30 &deg;C – min. 60 &deg;C

Dust/Water Protection: Min. IP 66

Environmental Type: Type B (outdoor application)

Speaker Component: Min. 8.9 cm x 4 woofer, min. 8.2 cm x 1 tweeter

Material: Aluminium enclosure and grill

Finish: White (RAL9016 or equivalent), paint

Dimension: Max. 610 (h) x max. 124 (w) x max. 108 (d) mm

Weight: Max. 3.9 kg