Product program / System Component / System Manager / Central Unit

VX-2000

Micro-processor based System Manager

Modular system for the distribution, control and monitoring. Audio matrix for the simultaneous transmission of 4 independent audio signals, as well as an audio signal to the listening. 8 Slots for various input modules for various sound sources such as microphones, CD player, cassette recorder, etc., 16 control inputs and 16 control outputs. 

Complete monitoring according to EN 60849 (VDE 0828), EN 54-16 and VDE 0833-4. 
Monitoring the CPU via the watchdog timer. Monitoring of critical internal and external audio signal paths. Audible and visual indication of all that occurred within about 100 seconds. 
Recording of the last 2000 actions and errors in the log for later error analysis and reconstruction of the processes on the system.

Two covered slots for text storage to the simultaneous transmission of warning and evacuation messages in separate areas of disaster or fire. 2-phase alarm (alarm with subsequent after adjustable time evacuation) can be programmed. Monitoring the availability of the texts and the text memory errors.

The basic volume of each input and output should be adjustable. Except the stations the volume levels of all inputs and outputs to either of the (s) stations or be adjustable via control inputs.

RS-232C interface for PC. PC-software under Windows ™ graphical user interface to the system configuration, system inspection and read out of the log. Automatic detection of system components. Timed automatic processes in daily, weekly and holiday programs can be programmed (timer recording). Expression of the system configuration documentation. Simple update system software without Exchange of EPROMs.

LED indicators for power, power supply on and error. Connector for external monitor speakers.