Product program / Power Supply / Emergency Power Supply

VX-3000DS CE

The Power Supply Manager shall supply DC power to individual public address/voice alarm system components. The Power Supply Manager shall be EN54-4 complied. It shall combine two built-in power source units with a high-performance charger in 3-unit size. Battery capacity per unit shall be Maximum 100 Ah (charging current:5.5A). It shall incorporate 31V/5A and 24V/0.3A DC power outputs as well as 31V/25A outputs for amplifiers. The removable terminal block shall save installation/maintenance time. If the Main AC power supply is down, the VX-3000DS switches automatically to auxiliary battery power. Fuse shall be able to be replaced from the rear panel without uninstalling the unit from a rack.
The Power Supply Manager shall operate on 220-230 AC, 50/60Hz, supply DC Power